## Sheet1
Name | Unit | Scaling | Bytes | # of Bytes | Index | Total size
SAP part number |  |  | 11 Byte | 11 | 0 | 159
SAP serial number |  |  | 18 Byte | 18 | 11
SAP date code |  |  | 4 Byte | 4 | 29
SAP revision |  |  | 2 Byte | 2 | 33
Software revision ac control | MA,MI |  | 2 Byte | 2 | 35
Software revision dc control | MA,MI |  | 2 Byte | 2 | 37
Software revision display | MA,MI |  | 2 Byte | 2 | 39
Software revision ens control | MA,MI |  | 2 Byte | 2 | 41
Solar current at input 1 | A | Value / 10 | 2 (MSB, LSB) | 2 | 43
Solar voltage at input 1 | V |  | 2 (MSB, LSB) | 2 | 45
Solar isolation resistance at input 1 | kOhm |  | 2 (MSB, LSB) | 2 | 47
Solar current at input 2 | A | Value / 10 | 2 (MSB, LSB) | 2 | 49
Solar voltage at input 2 | V |  | 2 (MSB, LSB) | 2 | 51
Solar isolation resistance at input 2 | kOhm |  | 2 (MSB, LSB) | 2 | 53
AC current | A | Value / 10 | 2 (MSB, LSB) | 2 | 55
AC voltage | V |  | 2 (MSB, LSB) | 2 | 57
AC power | W |  | 2 (MSB, LSB) | 2 | 59
AC frequency | Hz | Value / 1000 | 2 (MSB, LSB) | 2 | 61
Supplied ac energy | Wh |  | 2 (MSB, LSB) | 2 | 63
Inverter runtime | Minutes |  | 2 (MSB, LSB) | 2 | 65
Calculated temperature at ntc (DC side) | °C | Signed int16 | 2 (MSB, LSB) | 2 | 67
Solar input 1 MOV resistance | kOhm |  | 2 (MSB, LSB) | 2 | 69
Solar input 2 MOV resistance | kOhm |  | 2 (MSB, LSB) | 2 | 71
Calculated temperature at ntc (AC side) | °C | Signed int16 | 2 (MSB, LSB) | 2 | 73
AC voltage (AC control) | V | Value / 10 | 2 (MSB, LSB) | 2 | 75
AC frequency (AC control) | Hz | Value / 100 | 2 (MSB, LSB) | 2 | 77
DC injection current (AC control) | A | Value / 1000 | 2 (MSB, LSB) | 2 | 79
AC voltage (ENS control) | V | Value / 10 | 2 (MSB, LSB) | 2 | 81
AC frequency (ENS control) | Hz | Value / 100 | 2 (MSB, LSB) | 2 | 83
DC injection current (ENS control) | A | Value / 1000 | 2 (MSB, LSB) | 2 | 85
Maximum solar 1 input current | A | Value / 10 | 2 (MSB, LSB) | 2 | 87
Maximum solar 1 input voltage | V |  | 2 (MSB, LSB) | 2 | 89
Maximum solar 1 input power | W |  | 2 (MSB, LSB) | 2 | 91
Minimum isolation resistance solar 1 | kOhm |  | 2 (MSB, LSB) | 2 | 93
Maximum isolation resistance solar 1 | kOhm |  | 2 (MSB, LSB) | 2 | 95
Maximum solar 2 input current | A | Value / 10 | 2 (MSB, LSB) | 2 | 97
Maximum solar 2 input voltage | V |  | 2 (MSB, LSB) | 2 | 99
Maximum solar 2 input power | W |  | 2 (MSB, LSB) | 2 | 101
Minimum isolation resistance solar 2 | kOhm |  | 2 (MSB, LSB) | 2 | 103
Maximum isolation resistance solar 2 | kOhm |  | 2 (MSB, LSB) | 2 | 105
Maximum ac current of today | A | Value / 10 | 2 (MSB, LSB) | 2 | 107
Minimum ac voltage of today | V |  | 2 (MSB, LSB) | 2 | 109
Maximum ac voltage of today | V |  | 2 (MSB, LSB) | 2 | 111
Maximum ac power of today | W |  | 2 (MSB, LSB) | 2 | 113
Minimum ac frequency of today | Hz | Value / 100 | 2 (MSB, LSB) | 2 | 115
Maximum ac frequency of today | Hz | Value / 100 | 2 (MSB, LSB) | 2 | 117
Supplied ac energy | kWh | Value / 10 | 4 (MSB, LSB) | 4 | 119
Inverter runtime | Hours |  | 4 (MSB, LSB) | 4 | 123
Global alarm status |  |  | 1 Byte | 1 | 127
Status DC input |  |  | 1 Byte | 1 | 128
Limits DC input |  |  | 1 Byte | 1 | 129
Status AC output |  |  | 1 Byte | 1 | 130
Limits AC output |  |  | 1 Byte | 1 | 131
Isolation warning status |  |  | 1 Byte | 1 | 132
DC hardware failure |  |  | 1 Byte | 1 | 133
AC hardware failure |  |  | 1 Byte | 1 | 134
ENS hardware failure |  |  | 1 Byte | 1 | 135
Internal Bulk failure |  |  | 1 Byte | 1 | 136
Internal communications failure |  |  | 1 Byte | 1 | 137
AC hardware disturbance |  |  | 1 Byte | 1 | 138
History status messages |  |  | 20 Byte | 20 | 139
--- END --- |  |  |  |  | 159